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SWING DOOR OPERATORS
Profiler-ICU SmokeSwing™ Smoke Containment Barrier |  A18.00


	[bookmark: _Hlk152857433]Specification
	Selection

	Door ID
	

	Product Name
	Profiler-ICU SmokeSwing

	Design
	Edit Section 2.02.A

	Height
	  ‘Per Door Schedule’ 

	Width
	  ‘Per Door Schedule’ 

	Finish
	Edit Section 2.04.B

	Door Panel Materials
	Aluminum - Wall Thickness: 0.09”

	Stiles
	Edit Section 2.02.5.1

	Jamb Dimension
	1 3/4" (44mm) deep by 4" (102mm) high

	Bottom Rails
	Edit Section 2.02.5.2

	Muntin
	1/2” (13 mm)

	Threshold
	1/2" (13 mm) tall by 4” (102 mm) wide

	Header Size
	4" (102 mm) deep by 2 1/2" (63 mm) high


	Drive System
	Manual

	Locking
	Not Applicable

	Max Door Panel Weight
	Up to 200 lbs.

	Glazing Prep
	Edit Section 2.02.5.3

	Temperature Rating
	-30°F to 130°F

	Codes & Standards
	ANSI Z97.1, ANSI A117.1, NFPA 101, ASTM B221, ASTM B209, AAMA 611, AAMA 101, AAMA 701, ICC/IBC, BOCA, ICBO/UBC, AA, NAAMM, AAADM, UL 1784.




These specifications represent the exacting selection you have made for your project , including door configuration, colors and options and depict design features that are commonly used. Horton Automatics will custom manufacture each product to these specifications. It is the customer’s responsibility to validate that each configuration is suitable for the intended application. All specifications and designs contained herein are subject to change without notice or obligation. Consult www.hortondoors.com’ spec desk at 1-800-531-3111 for assistance.


DIVISION 08 - OPENINGS
SECTION 08 42 43 – INTENSIVE CARE UNITS / CRITICAL CARE UNIT ENTRANCES
PART I – GENERAL

1.01 SUMMARY

A. WORK INCLUDED: 	
Furnish exterior and interior power door operators with visible mounting, as specified, that has been manufactured, fabricated, and installed to maintain performance criteria stated by manufacturer without defects, damage or failure. 
B. RELATED WORK:
1. Division 4 Sections for masonry, applicable sections.
2. Division 7 Sections for caulking, applicable sections.
3. Division 8 Sections for aluminum-framed entrances and storefronts for entrances furnished separately.
4. Division 8 Section "All-Glass Entrances and Storefronts" for entrances furnished separately.
5. Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.
6. Division 8 Section "Glazing" for materials and installation requirements. 

1.02 REFERENCES
A. American National Standards Institute (ANSI):
1. ANSI Z97.1: Safety Glazing Materials Used in Buildings - Methods of Test
2. ANSI A117.1: Accessible and Usable Buildings and Facilities
B. National Fire Protection Association (NFPA):
1. NFPA 101: Safety to Life from Fire in Buildings & Structures
2. NFPA 105: Standard for the Installation of Smoke Door Assemblies and Other Opening 
C. ASTM International:
1. ASTM B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes
2. ASTM B209: Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate
D. American Architectural Manufacturers Association (AAMA):
1. AAMA 611: Voluntary Specification for Anodized Architectural Aluminum
2. AAMA 101: Appendix Dissimilar Materials	
E. International Code Council (ICC): ICC/IBC: International Building Code
F. Building Officials and Code Administrators International (BOCA)
G. International Conference of Building Officials / Uniform Building Code (ICBO/UBC)
H. INTERTEK, WARNOCK HERSEY: Testing Laboratory and Certification Agency in partnership with ETL SEMKO  Testing and Certification includes, but is not limited to, Smoke Containment Barrier Doors as per performance criteria of UL 1784.
I. Aluminum Association (AA):
1. AA: Aluminum Finishes Manual
J. National Association of Architectural Metal Manufacturers (NAAMM)
K. American Association of Automatic Door Manufacturers (AAADM)
L. Underwriters Laboratories (UL): 1784 Air Leakage Test of Door Assemblies.


1.03 SUBMITTALS
A. SHOP DRAWINGS & PRODUCT DATA 
1. Provide product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions, and finishes.
2. Include plans, elevations, sections, details, hardware mounting heights, additional accessories, and attachments to other work. 
3. Submit drawings showing layout, profiles, product components including anchorage, accessories, finish, and glazing details (where required)
4. Samples:  Color samples for selection of factory-applied color finishes will be provided as request.
5. Environmental & Sustainability Information: 
a. Manufacturer's product information and applicable sustainability program credits that are available towards a LEED rated product certification.
b. Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each product specified under this section.

B. CLOSEOUT SUBMITTALS: 
Owner’s Manual & Warranty document as specified herein. 
Operating and Maintenance Manuals: Provide manufacturers operating, owners and maintenance manuals for each item specified as required. Include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives. The final copies delivered after completion of the installation test to include spare parts list. 

1.04 QUALITY ASSURANCE

A. Installers Qualifications: Installer shall be factory trained, certified by AAADM, and experienced to perform work of this section.
B. Manufacturer's Qualifications: 
1. Manufacturer to have minimum of (5) five years successful experience in the fabrication of automatic doors of the type required for this project. 
2. Manufacturer capable of providing field service representation during installation, approving acceptable installer, and approving the application method.

C. Certifications: door systems and options shall be factory certified to meet performance design criteria in NFPA 101: Code for Safety to Life from Fire in Buildings & Structures.
1. [bookmark: _Hlk156392999]#ADA 1990: Americans with Disability Act 

D. PERFORMANCE REQUIREMENTS:
1. Operating Temperature Range: Capable of -30° F to 130° F (-34° C to 54° C).

1.05 PROJECT CONDITIONS

A. Field Measurements:
Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

B. On-Site Field Conditions Required Prior to Installation:
1. Approved Shop drawings must be referenced and confirmed by the General Contractor before fabrication.
2. Opening must be verified to be plumb, straight, and secure.
3. It is the duty of the General Contractor to make door installer aware of any nonconforming conditions or equipment as indicated on the shop drawings.
4. General Contractor is required to coordinate the layout and installation of the automatic door equipment connection to power supplies.
5. Mounting Surfaces: General Contractor shall verify all surfaces to be plumb, straight, and secure; substrates to be of proper dimension and material.
6. General Contractor shall advise of any inadequate conditions or equipment.

1.06 DELIVERY, STORAGE AND HANDLING
A. Ordering and Delivery: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. Storage and Protection: Provide protection from exposure to harmful weather conditions and vandalism

1.07 WARRANTIES
A. Warranty Period: 2-year warranty: Labor & transportation costs covered for replacement of parts defective in material and workmanship from the Date of Substantial Completion.

B. Distributor's Warranty: 1-year warranty: Labor & transportation charges for defective parts replacement 

C. Service and Repairs: 
1. During the warranty period, a factory-trained technician shall perform service and affect repairs.
2. A safety inspection shall be performed after each adjustment or repair and a completed inspection form submitted to the owner.

D. Warranty Work Hours: During the warranty period, all warranty work shall be performed during normal working hours by our distribution networks.

[bookmark: _heading=h.30j0zll]PART II – PRODUCTS

2.01 MANUFACTURER
[bookmark: _Hlk152857477]Basis of design: Horton Automatics, a division of Overhead Door Corporation, shall manufacture automatic sliding door(s) of type(s) and size(s) specified on plans and door schedule. 4242 Baldwin Blvd, Corpus Christi, TX 78405. Toll Free: 361-866.6603 www.hortondoors.com. hortonautomatics@overheaddoor.com. 

☐.[Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

☒.[Substitutions:  Not Permitted.]

[bookmark: _heading=h.1fob9te]2.02 EQUIPMENT
A. 	MANUFACTURED DOOR UNITS: Shall include header, jambs and swing panel(s) {CHOOSE 1}:
 1. Unequal Pair: one wide swing panel (primary egress) and one narrow swing panel (auxiliary egress) normally fixed. 
2. Pair: two wide swing panels (both primary egress or primary/auxiliary combination)
3. Single: wide swing panel (primary egress)

B. 	INSTALLATION: The operator header shall be mounted to the surface of the existing labeled door frame or wall. Connecting hardware shall be a double arm arrangement that pushes the existing labeled door open. UL approved “Fire Exit Hardware” shall be supplied by others and shall be type GXHX as found in the UL Materials Directory. This equipment shall work in conjunction with fire/smoke detection system provided by others.

C. AIR INFILTRATION RATING: Units tested and certified by Intertek to be in compliance with UL 1784. Maximum leakage rate at ambient temperature shall be less than 2 CFM/ft2 of opening at 0.3 in. of water. At 400°F the rate of leakage shall be less than 1 CFM/ft² of opening at 0.3 in. of water.

C. 	HEADER: Shall be aluminum with removable faceplate. Header size to be 4" (102 mm) deep by 2 1/2" (63 mm) high. 
 
D.	SWING PANELS: Shall be aluminum, Shall be aluminum, 1-3/4" (44 mm) deep with narrow stile construction with 10” bottom rail. Weather-stripping to be along perimeter of panel. Glazing prep to be for 1/4” (6 mm) glass. Panels to be wet glazed with red high temperature silicone sealant at corners.
. 
1. 	Main Egress Panel (wide panel): Shall be provided with positive latch that will latch this panel in place when closed. A lever handle shall be provided on each side of the panel to unlock and swing open door. 
2. 	Auxiliary Egress Panel (narrow panel): Shall be provided with a constant latching flush bolt to lock this panel in place when closed. Flush bolt to be manually released to unlock and swing open door. 
3. 	Swing panels shall swing open after positive latching or locking released and require no more than 30 lbf.   (133 N) of force applied at the strike stile to open. 
4. 	Units are compliant with NFPA 101.
5. Optional construction shall include:
1. Rail Stiles {CHOOSE 1}:
a. Narrow stile rails (default)
b. Medium stile rails
c. Wide stile rails 
2. Bottom Rail Options {CHOOSE 1}:
a. 4” bottom rails 
b. 6 1/2" bottom rails 
c. 8" bottom rails.
3. Custom glazing prep {CHOOSE 1}:
d. 1/4" (6mm) default
e. 3/8" (10mm)
f. 1/2" (13mm)
g. 1" (25mm)
h. Unicel Glazing by Others

E. JAMBS/FRAME: 
Shall be aluminum, 1 3/4" (44 mm) deep by 4" (102 mm) wide x .125” thickness.

2.03 RELATED EQUIPMENT
GLASS AND GLAZING: Glazing materials: glass stops, glazing vinyl and setting blocks for field glazing as per safety glazing standard ANSI Z97.1.2 and UL 1784. General contractor to coordinate acquisition of glass in thickness and type in accordance with manufacturer's recommendations for prescribed design.

2.04 MATERIALS, FINISHES, AND FABRICATION EXTRUDED ALUMINUM:
A. EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:
1. 	Structural Header Sections: Minimum 3/16" (5 mm) thickness.
2. 	Structural Frame Sections: Minimum 1/8" (3 mm) thickness.
3. 	Structural Panel Sections: Minimum 1/8" (3 mm) thickness.

[bookmark: _heading=h.1ksv4uv]B. FINISH (for all exposed aluminum surfaces): Shall be one of the following:
1. 	204-R1 Clear: Arch. Class 2 Clear Anodized Coating, AA-MI2C22A31.
2. 	313-R1 Dark Bronze: Arch. Class 1 Anodized Coating, AA-MI2C22A44.
3. 	312-R1 Light Bronze: Arch. Class 1 Anodized Coating, AA-MI2C22A44.
4. 	315-R1 Black: Arch. Class 1 Anodized Coating, AA-MI2C22A44.
5. 	Special Paint Coating: Color as selected.
[bookmark: _heading=h.35nkun2]	
C. PANEL CONSTRUCTION: 
1.	Corner block type with 3/16” steel backup plate construction, mechanically secured with minimum of four hardened steel screws. Sash consists of snap-in glass stops, snap-in glazing beads and vinyl gaskets. Gasketing material is high temperature silicone and is to be captured in extruded aluminum door panel. Floor Smoke Seal is high temperature brush. All seals to be factory installed to maintain UL 1784 rating.
2.	Panel to be supplied with adjustable glass setting block to allow for adjusting of door to meet site conditions eliminating the need for additional shims.

D. 	FRAME CONSTRUCTION: Butt joints mechanically secured by means of screws and formed aluminum corner brackets.

[bookmark: _Hlk152857526]
PART III - EXECUTION
3.01 EXAMINATION
SITE VERIFICATION OF CONDITIONS:
1. The installer shall verify that the base conditions meet the manufacturer's instructions for product installation. Any negative conditions that may affect the proper and timely completion of work must be notified to the Contractor in writing. All negative conditions must be corrected in a manner acceptable to the manufacturer.
2. With the installer present, examine doors and frames for compliance with installation tolerances, wall and floor construction, and other conditions affecting performance.
3. Verify the actual locations of wiring connections for roughing-in electrical source power.
4. The installer must correct all unsatisfactory conditions before proceeding with the installation.
3.02 INSTALLATION
A. ENTRANCES: 
Install automatic entrances plumb and true in alignment with established lines and grades without warp or crack of framing members and doors. Use concealed fasteners to the greatest extent possible for surface-mounted hardware.
Set headers, carrier assemblies, tracks, operating brackets, and guides level and true to location with anchorage for permanent support.

B. GLAZING: 
Install glazing according to the automatic door manufacturer's instructions, the Glass Association of North America (GANA) Glazing Manual, and glass product manufacturer recommendations.

C. SEALANTS: 
Use sealants to comply with the requirements specified in Division 7 Section "Joint Sealants" to provide a weather-tight installation. Set thresholds, bottom guide and track systems, and framing members in full bed of sealant.

D. DISSIMILAR MATERIALS: 
Separate aluminum materials and other corrodible surfaces from sources of corrosion or electrolytic action contact points to comply with AAMA 101, Appendix Dissimilar Materials.

E. SMOKE CONTAINMENT BARRIER CONSTRUCTION: 
Install header and framing members in a bed of neutral cure silicone sealant to maintain compliance with NFPA 105. Coordinate installation with wall flashings and other components of construction.

G. SIGNAGE:
Apply signage on both sides of each door as required by manufacturer’s installation instruction 

3.03 CLEANING, ADJUSTMENT, AND PROTECTION
A. CLEANING AND ADJUSTMENT: 
1. Remove temporary protection of adjacent work areas. Remove construction debris from construction site and legally dispose of debris. Repair or replace damaged installed products. Clean product surfaces and lubricate operating equipment for optimum condition and safety.
2. Adjust door operators, controls, and hardware for smooth and safe operation 
3. Verify installation and alignment of all entrance weather-stripping as required.
B. ADVISE CONTRACTOR: Of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration (other than normal weathering) at the time of acceptance.
3.04  FIELD QUALITY CONTROL
Manufacturer’s representative shall provide technical assistance and guidance for installation of automatic doors. Factory trained representative shall test and inspect each automatic door to determine compliance of the installed system with applicable standards.
3.05 INSTRUCTION
Following the installation and final adjustments, the installer shall fully instruct the facility manager as to the correct operating procedure and safety requirements of the sliding door package.

END OF SECTION

Horton Automatics reserves the right to make product improvements and change specifications without notice.



[image: ]

Section 08 42 43 


image1.png
Horton

Horton Automatics
World Headquarters

4242 Baldwin Boulevard

Corpus Christi, Texas 78405-3399 USA
Tel: 800-531-3111, 361-888-5591

Fax: 800-531-3108, 361-888-6510




