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AUTOMATIC SLIDING ENTRANCES
Profiler®-ICU MAX/XM  Self-Closing IDS Smoke Rated Manual Isolation Door System
Single Slide with Trackless Guide – 7’ to 9’ Single Slide
 Compliant with ISO 14644 Class 3 Cleanrooms | A29.01


	[bookmark: _Hlk152857433]Specification
	Selection

	Door ID
	{door_ID}

	Product Name
	Profiler®-ICU MAX/XM Self-Closing IDS Smoke Rated Manual Isolation Door System Single Slide with Trackless Guide

	Design {CHOOSE 1}
	O-SX, SX-O, P-SX, SX-P, SO-SX, SX-SO, TBD

	Breakout
	Type 110 or 310 – Partial or Full breakout

	Height
	Per door schedule. Specifiable width: 7’ to 9’ – single slide only

	Width
	Per door schedule. Specifiable height: up to 7’6”

	Finish
	{finish}. {anodize_finish}{painted_finish}{clad_finish}. {color_w}{color_p}

	Door Panel Materials
	Aluminum - Wall Thickness : {thickness}

	Stiles
	1 3/4" (44mm) deep with narrow with perimeter seals

	Jamb Dimension
	1 3/4" (44mm) deep by 4" (102mm) wide

	Muntin
	2 1/4" (57mm) wide

	Bottom Rail
	Standard 4” (102mm) – Specifiable: 6 ½” (165mm) and 10” (254mm)

	Header Size
	4” (102mm) x 6” (152mm)

	Drive System
	Manual

	Activation/Safety Sensors
	N/A – Manual Operation

	Locking
	Positive lathing required for UL1784 compliance

	Max Door Panel Weight
	Up to 200 lbs.

	Glazing Prep
	{glazing}

	Temperature Rating
	-30°F to 130°F

	Codes & Standards
	{code}.


These specifications represent the exacting selection you have made for your project {PROJECT}, including door configuration, colors and options and depict design features that are commonly used. Horton Automatics will custom manufacture each product to these specifications. It is the customer’s responsibility to validate that each configuration is suitable for the intended application. All specifications and designs contained herein are subject to change without notice or obligation. Consult www.hortondoors.com’ spec desk at 1-800-531-3111 or specs@hortondoors.com for assistance.




DIVISION 08 - OPENINGS
SECTION 08 42 43 – INTENSIVE CARE UNITS / CRITICAL CARE UNIT ENTRANCES

PART I – GENERAL
1.01 SUMMARY
A. WORK INCLUDED: 
Furnish specified complete automatic door system manufactured, fabricated & installed to meet manufacturer’s specifications and applicable codes at the time of purchase.
B. RELATED WORK:
1. Division 7 Sections for caulking to the extent not specified in this section.
2. Division 8 Sections for aluminum-framed entrances and storefronts for entrances furnished separately.
3. Division 8 Section "All-Glass Entrances and Storefronts" for entrances furnished separately.
4. Division 8 Section "Door Hardware" for hardware to the extent not specified in this Section.
5. Division 8 Section "Glazing" for materials and installation requirements of glazing for automatic entrances. 
6. Division 26 Sections for electrical connections provided separately including conduit and wiring for power to, and control of, automatic door operators.

[bookmark: _Hlk148367541]1.02 REFERENCES
A. American National Standards Institute (ANSI):
1. ANSI Z97.1: Safety Glazing Materials Used in Buildings - Methods of Test
2. ANSI A117.1: Accessible and Usable Buildings and Facilities
3. ANSI A156.5: Standard for Auxiliary Locks and Associated Products
B. National Fire Protection Association (NFPA):
1. NFPA 101: Safety to Life from Fire in Buildings & Structures
C. ASTM International:
1. ASTM B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes
2. ASTM B209: Standard Specification for Aluminum and Aluminum Alloy Sheet and Plate
D. American Architectural Manufacturers Association (AAMA):
1. AAMA 611: Voluntary Specification for Anodized Architectural Aluminum
2. AAMA 701: Voluntary Specification for Pile Weatherstripping and Replaceable Fenestration Weatherseals
E. International Code Council (ICC): ICC/IBC: International Building Code
F. Building Officials and Code Administrators International (BOCA)
G. International Conference of Building Officials / Uniform Building Code (ICBO/UBC)
H. Intertek, Warnock Hersey (ETL): Testing Laboratory and Certification Agency joined with ETL SEMKO
I. International Organization for Standardization (ISO):
1. ISO 9001: Quality Management Systems
2. ISO 14644-1, Class 3: Cleanrooms & controlled environments, Classification of air cleanliness by particle concentration.
J. Aluminum Association (AA): Aluminum Finishes Manual
K. National Association of Architectural Metal Manufacturers (NAAMM)
L. American Association of Automatic Door Manufacturers (AAADM)
1. Underwriters Laboratories (UL): UL 1784: Air Leakage Test of Door Assemblies
M. 2018 FACILITIES GUIDELINES INSTITUTE (FGI) FOR DESIGN AND CONSTRUCTION OF AIRBORNE INFECTION ISOLATION ROOMS (AIIR) IN HEALTHCARE FACILITIES(FGI): Ref: A2.1-7.2.2.3 (2)(a)(i) Minimum Slide Door Opening Width

1.03 SUBMITTALS
A. SHOP DRAWINGS & PRODUCT DATA 
1. Provide product data sheets including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions, and finishes.
2. Include plans, elevations, sections, details, hardware mounting heights, additional accessories, and attachments to other work. 
3. Submit drawings showing layout, profiles, product components including anchorage, accessories, finish, and glazing details (where required)
4. Samples:  Color samples for selection of factory-applied color finishes will be provided as request.
5. Environmental & Sustainability Information: 
a. Environmental Product Declaration 
b. Manufacturer's product information and applicable sustainability program credits that are available towards a LEED rated product certification.
c. Credit MR 4.1 and 4.2: Manufacturer's or fabricator's certificate indicating percentage of post-consumer recycled content by weight and pre-consumer recycled content by weight for each product specified under this section.
6. AAADM Inspection & Reports:  AAADM inspection compliance form completed and signed by a certified AAADM inspector prior to doors being placed in operation as proof of compliance with ANSI A156.10 

B. CLOSEOUT SUBMITTALS: 
Owner’s Manual & Warranty document as specified herein. Operating and Maintenance Manuals: Provide manufacturers operating, owners and maintenance manuals for each item specified as required. Include the name, address, and contact information of the manufacturers providing the entrance and their nearest service representatives. The final copies delivered after completion of the installation test to include spare parts list. 

1.04 QUALITY ASSURANCE
A. INSTALLERS QUALIFICATIONS: Installer shall be factory trained and experienced to perform work of this section and who is acceptable to the product manufacturer.

B. MANUFACTURER'S QUALIFICATIONS: 
1. Manufacturer to have minimum of (5) five years successful experience in the fabrication of doors of the type required for this project. 
2. Manufacturer capable of providing field service representation during installation, approving acceptable installer, and approving the application method.

C.	CERTIFICATIONS: Manual sliding door systems to be certified in accordance with the following standards:
1.	NFPA 105: Standard for the Installation of Smoke Door Assemblies and Other Opening Protectives.
2.	ETL LISTED AIR INFILTRATION RATING: Units tested and certified by Intertek to be in compliance with ASTM E283-04 and UL 1784:
a.	Maximum leakage rate at ambient temperature: 3.00 CFM/ft2 of opening at 0.3 in. of water.
b.	Maximum leakage rate at 400° F: 3.00 CFM/ft2 of opening at 0.3 in. of water.

D. 	FGI GUIDELINES COMPLIANCE: A2.1-7.2.2.3 (2)(a)(i) 45.5” Minimum Door Opening Width

E.	OPENING FORCE REQUIREMENTS: Standard slide panels glazed with ¼” tempered glass can be slid open with 8-12 lbs. of force after positive latch released.
[bookmark: _Hlk16603779]1.	Breakaway Requirements: Slide-swing panels shall swing out 90° from fully open position after
positive latching and flush bolt released and require no more than 50 lbf. (222 N) of force applied at the strike stile to open.

F. HEADER CAPACITY: Up to 350 lbs. (158.7 kg) per slide panel over spans

1.05 PROJECT CONDITIONS
A. FIELD MEASUREMENTS:
Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

B. ON-SITE FIELD CONDITIONS REQUIRED PRIOR TO INSTALLATION:
1. Approved Shop drawings must be referenced and confirmed by the General Contractor before fabrication.
2. Opening must be verified to be plumb, straight, and secure.
3. It is the duty of the General Contractor to make door installer aware of any nonconforming conditions or equipment as indicated on the shop drawings.
4. General Contractor is required to coordinate the layout and installation of the automatic door equipment connection to power supplies.
5. Mounting Surfaces: General Contractor shall verify all surfaces to be plumb, straight, and secure; substrates to be of proper dimension and material.
6. General Contractor shall advise of any inadequate conditions or equipment.

1.06 DELIVERY, STORAGE AND HANDLING
A. ORDERING AND DELIVERY: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. STORAGE AND PROTECTION: Provide protection from exposure to harmful weather conditions and vandalism

1.07 WARRANTIES
A. WARRANTY PERIOD: 2-year warranty: Labor & transportation costs covered for replacement of parts defective in material and workmanship from the Date of Substantial Completion.

B. DISTRIBUTOR'S WARRANTY: 1-year warranty: Labor & transportation charges for defective parts replacement 

C. SERVICE AND REPAIRS: 
1. During the warranty period, a factory-trained technician shall perform service and affect repairs.
2. A safety inspection shall be performed after each adjustment or repair and a completed inspection form submitted to the owner.

D. WARRANTY WORK HOURS: During the warranty period, all warranty work shall be performed during normal working hours by our distribution networks.

[bookmark: _heading=h.30j0zll]PART II – PRODUCTS
2.01 MANUFACTURER
[bookmark: _Hlk152857477]Basis of design: Horton Automatics, a division of Overhead Door Corporation, shall manufacture automatic sliding door(s) of type(s) and size(s) specified on plans and door schedule. 4242 Baldwin Blvd, Corpus Christi, TX 78405. Toll Free: 800-531.3111 www.hortondoors.com. specs@hortondoors.com/
 
☐.[Substitutions:  Requests for substitution and product approval in compliance with the specifications must be submitted in writing and in accordance with the procedures outlined in Division 1, Section “Substitution Procedures”.  Approval of requests is at the discretion of the architect, owner, and their designated consultants.]

☒.[Substitutions:  Not Permitted.]

[bookmark: _heading=h.1fob9te]2.02 EQUIPMENT
A. Dimensions: {CHOOSE 1}
· Exact Dimensions:
Enter Width [opening with minus ½”]:
      	Enter Height [to top of the header]
· Follow door schedule

2.02.01. DOOR ASSEMBLIES
A. MANUFACTURED DOOR UNITS: Shall Profiler ICU Self Closing IDS and include operator, header with roller track, carrier assemblies, framing, sliding door panel(s), sidelite(s), activation, safety devices and accessories required for complete installation. Units to provide minimum of 45 1/2" (1156mm) of clear slide opening width in compliance with 2018 FGI Guidelines for Airborne Infection Isolation Rooms (AIIR).

1. [bookmark: _heading=h.3znysh7][bookmark: _Hlk153824475]Configuration: Single Slide [one sliding panel and one non-sliding panels]
1. Mounting Type {CHOOSE 1}
· Perimeter mounted within rough opening with sliding panel(s) sliding along sidelite. 
· Surface mounted with sliding panel(s) sliding along wall eliminating need for sidelite.
2. Hand {CHOOSE 1}
· Perimeter mounted: {CHOOSE 1: SO-SX, SX-SO. 0-SX, SX-O}
· Surface mounted {CHOOSE 1: P-SX, SX-P}

B. DEFINITIONS
1. SO panel: stationary sidelite capable of swinging away for emergency egress
2. SX panel: sliding panel capable of swinging away for emergency egress
3. O panel: a fixed panel with no capability to either slide or swing away
4. Single Slide: a door system with one stationary panel and one moving panel that open/closes on one side. The moving and stationary panels overlap when the door is open.
5. Bi-Parting Slide: a door system with two moving panels that slide in opposite directions with two stationary panels that overlap the slide panels when the door is open 
6. [bookmark: _heading=h.2et92p0]Type 010 – non breakout: Sliding panel(s) ‘X’ shall slide along interior side.
7. Type 110 – partial breakout: Slide-swing panel(s) ‘SX’ shall slide along exterior ‘O’ fixed sidelite(s).
8. Type 310 – full breakout: Slide-swing panel(s) ‘SX’ shall slide along interior ‘SO’ swing-out sidelite(s)
9. Type 310 Trackless: Slide-swing panel ‘SX’ shall slide along interior side of swing-out sidelite ‘SO’ (door must be in full open position) utilizing trackless floor system with no floor track/guide or recess required.

2.02.02 COMPONENTS
A. HEADER: 
1. [bookmark: _heading=h.1t3h5sf]Shall be slim, 4” (102mm) x 6” (152mm) aluminum construction.
2. The header shall have a removable face plate for service and adjustment of the operator and controls.
3. The header mounts flush to 4” framing jambs.

B. CARRIER ASSEMBLIES AND HEADER ROLLER TRACK:
1. Telescoping doors will have two separate tracks for sliding panels to travel. 
2. Rollers will be steel, high quality ball bearing wheels 1-1/4" (32 mm) diameter. 
3. Anti-Derailing (anti-raise) shall be accomplished by means of a continuous aluminum extrusion full length of slide panel travel. The overhead header roller track shall be continuous aluminum, nylon covered, and replaceable.

C. SLIDING PANEL(S) AND SIDELITE(S):
[bookmark: _heading=h.4d34og8]Minimum Door Panel Extrusion Thickness : 0.09” {OPTIONAL: 0.125”]
1. Stile: Shall be aluminum: 1-3/4" (44 mm) deep
[bookmark: _Hlk148360354]Muntin Bar:  An intermediate horizontal rail, shall be furnished for safety and division of glass. 2-1/4" (57 mm) 
[bookmark: _heading=h.2s8eyo1]Bottom rail:  Shall be Narrow {CHOOSE 1}:
4" (102 mm) (default)
6 1/2" (165 mm)
10" (254 mm)
2. Concealed guides to stabilize bottom of sliding panel.
3. Sidelites: Additional and/or extra wide of size and type indicated.
4. Track and non-threshold application.
5. Sliding panels shall have concealed bottom guides to stabilize slide travel.
6. Weather-stripping: Along perimeter of sliding panel(s) and swing-out sidelite(s). Weatherstripping material captured in extruded aluminum door panel. Surface applied self-adhesive weatherstripping not acceptable. Adjustable spring-loaded double astragal weather-stripping at lead edge, double mohair at interlock rails.
7. Floor Seals to be field applied and adjusted from 1/8" to 1/2" above finished floor to required positive/negative pressure
8. Finger Safety: Strike rail of sliding panel will stop short of adjacent sidelite.
9. Weight Limit: The total weight limit per panel shall be:
a. 200 lbs. (90.7 kg) for slide panel (non-breakout)
b. 156 lbs. (70.7 kg) for slide-swing panel

D. BREAKOUT PANELS:
1. Swing-out Feature: In fully open position after positive latch and flush bolt is released, panels can swing out 90° with maximum 50 lbs. of force applied at the strike rail. Breakout mechanism shall provide support across full width of the door, in normal operating mode. In breakout mode, torsion assembly shall support weight of the door to minimize drop.
2. Positive Latch: shall be provided on slide-swing panel. Panel will latch in place when closed. A lever handle shall be provided on each side of this sliding panel to unlock the door. This specification: Positive latching: {positive_latching}. Optional antimicrobial coating available for lever handle shall be available.
3. Constant Latching Flush Bolt: shall be provided for swing-out sidelite. Swing-out sidelite will thus be locked in place under normal conditions. 
4. Units with a breakout feature are ETL listed as an exit away and are compliant with NFPA 101.

[bookmark: _heading=h.17dp8vu]E. JAMBS/FRAME: Shall be aluminum, 1 3/4" (44mm) deep x 4 1/2" (114mm) high

G. GLASS AND GLAZING: 
Glass stops, glazing vinyl and setting blocks for field glazing as per Safety Glazing standard ANSI Z97.1.2. Glazing prep to be for {CHOOSE 1}:
1/4" (6mm) default
3/8" (10mm)
1/2" (13mm)
5/8" (16mm)
3/4" (19mm)
1" (25mm)

2.02.05 MATERIALS, FINISHES, AND FABRICATION EXTRUDED ALUMINUM:
A. EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:
1. 	Structural Header Sections: Minimum 3/16" (5 mm) thickness.
2. 	Structural Frame Sections: Minimum 1/8" (3 mm) thickness.
3. 	Structural Panel Sections: Minimum 1/8" (3 mm) thickness.
[bookmark: _heading=h.35nkun2]
[bookmark: _heading=h.1ksv4uv]B. FINISH: {CHOOSE FROM 1, 2 OR 3 BELOW}
1. If Anodize Finish {CHOOSE 1}:
· 204-R1 Clear: Architectural Class 1 Clear Anodized Coating, AA-MI2C22A31.
· Champagne: Architectural Class 1 Anodized Coating, AA-MI2C22A44.
· 311-R1 Light Bronze: Architectural Class 1 Anodized Coating, AA-MI2C22A44.
· 312-R1 Medium Bronze: Architectural Class 1 Anodized Coating, AA-MI2C22A44.
· 313-R1 Dark Bronze: Architectural Class 1 Anodized Coating, AA-MI2C22A44.
· Black: Architectural Class 1 Anodized Coating, AA-MI2C22A44.
2. If Paint finish {CHOOSE 1}:
· Powder Coat: 100% V.O.C. free fluoropolymer resin-based. Color Code TBD.
· Wet Paint: Color Code TBD.
3. If Clad Finish {CHOOSE 1}:
· Stainless Steel #4 (Satin Finish): Architectural Satin Finish Clad Coating.
· Stainless Steel #8 (Mirror Finish): Architectural Reflective Clad Coating.
· Bronze #4 (Satin Finish): Architectural Satin Finish Clad Coating.
· Bronze with Polish (Non-Directional Finish): Architectural Non-Directional Polished Clad Coating.
· Brass #4 (Satin Finish): Architectural Satin Finish Clad Coating.
· Brass with Polish (Non-Directional Finish): Architectural Non-Directional Polished Clad Coating.
· Muntz Metal (Brass Alloy): Architectural Clad Coating.

C.	PANEL CONSTRUCTION: 	
1.	Corner block type with 3/16” steel backup plate construction, mechanically secured with minimum of four hardened steel screws and threaded rod reinforcement. Sash consists of snap-in glass stops, snap-in glazing beads and vinyl gaskets. Unlike common thru-bolt designs, corner blocks prevent distortion of the door panels during use and abuse.
2.	Slide-swing doors to be supplied with adjustable glass setting block to allow for adjusting of door to meet site conditions eliminating the need for additional shims. 
3.	Adjustable double astragal with dual weatherstrip physically captured for superior seal standard (adhesive applied weatherstrip not acceptable)

D.  FRAME CONSTRUCTION: Butt joints, mechanically secured with screws and formed alum. corner brackets.

PART III - EXECUTION
3.01 EXAMINATION
SITE VERIFICATION OF CONDITIONS:
1. The installer shall verify that the base conditions meet the manufacturer's instructions for product installation. Any negative conditions that may affect the proper and timely completion of work must be notified to the Contractor in writing. All negative conditions must be corrected in a manner acceptable to the manufacturer.
2. With the installer present, examine doors and frames for compliance with installation tolerances, wall and floor construction, and other conditions affecting performance.
3. Verify the actual locations of wiring connections for roughing-in electrical source power.
4. The installer must correct all unsatisfactory conditions before proceeding with the installation.

3.02 INSTALLATION 
A. ENTRANCES: 
Install automatic entrances plumb and true in alignment with established lines and grades without warp or crack of framing members and doors. Use concealed fasteners to the greatest extent possible for surface-mounted hardware. Set headers, carrier assemblies, tracks, operating brackets, and guides level and true to location with anchorage for permanent support.

B. DOOR OPERATORS: 
Connect door operators to the electrical power distribution system as specified in Division 26 Sections.

C. GLAZING: 
Install glazing according to the automatic door manufacturer's instructions, the Glass Association of North America (GANA) Glazing Manual, and glass product manufacturer recommendations.

D. SEALANTS: 
Use sealants to comply with the requirements specified in Division 7 Section "Joint Sealants" to provide a weather-tight installation. Set thresholds, bottom guide and track systems, and framing members in full bed of sealant.

E. DISSIMILAR MATERIALS: 
Separate aluminum materials and other corrodible surfaces from sources of corrosion or electrolytic action contact points to comply with AAMA 101, Appendix Dissimilar Materials.

3.03 CLEANING, ADJUSTMENT, AND PROTECTION
A. CLEANING AND ADJUSTMENT: 
1. Remove temporary protection of adjacent work areas. Remove construction debris from construction site and legally dispose of debris. Repair or replace damaged installed products. Clean product surfaces and lubricate operating equipment for optimum condition and safety.
2. Adjust door operators, controls, and hardware for smooth and safe operation 
3. Verify installation and alignment of all entrance weather-stripping as required.

B. ADVISE CONTRACTOR: Of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration (other than normal weathering) at the time of acceptance.

3.04 FIELD QUALITY CONTROL
Manufacturer’s representative shall provide technical assistance and guidance for installation of automatic doors. Factory trained representative shall test and inspect each automatic door to determine compliance with applicable codes.

3.05 INSTRUCTION
Following the installation and final adjustments, the installer shall fully instruct the facility manager as to the correct operating procedure and safety requirements of the sliding door package.

END OF SECTION

Horton Automatics reserves the right to make product improvements and change specifications without notice.
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