DIVISION 08 - OPENINGS

SECTION 08 42 43 – INTERMEDIATE / INTENSIVE / CRITICAL CARE UNIT ENTRANCES

Specifier Note: Coordinate and edit articles and paragraphs below to suit project requirements. Add section numbers and titles per CSI "MasterFormat" and specifier's practice. Consult with manufacturer regarding performance requirements for units applicable to project, as well as, related equipment and accessories required.

PART I – GENERAL

1.01 SUMMARY

A. 	WORK INCLUDED: Furnish specified barn door type manual door system, that has been manufactured, fabricated & installed to meet manufacturer’s standards without defects, damage or failure.

B. 	RELATED WORK: Openings: Division 08, applicable sections.

1.02 REFERENCES

A. 	THE ALUMINUM ASSOCIATION (AA) Aluminum Finishes Manual.

B.	AMERICAN ARCHITECTURAL MANUFACTURERS ASSOCIATION (AAMA) 101: Dissimilar Materials.

C. 	AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI) Z97.1: Safety Glazing Materials Used in Buildings.

D. 	AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM) B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes.

E. 	NATIONAL FIRE PROTECTION ASSOCIATION (NFPA) 101: Code for Safety to Life from Fire in Buildings & Structures.

1.03 SUBMITTALS

A. 	SHOP DRAWINGS & PRODUCT DATA: Submit drawings and product data showing layout, profiles, product components including anchorage, accessories, finish and glazing details (where required).

B. 	CLOSEOUT SUBMITTALS: Submit Owner’s Manual & Warranty document as specified herein. Submit AAADM inspection compliance form completed and signed by certified AAADM inspector prior to doors being placed in operation as proof of compliance with ANSI A156.38.

1.04 QUALITY ASSURANCE

A. 	INSTALLERS QUALIFICATIONS: Installer experienced to perform work of this section who has specialized in the installation of work like that required for this project and who is acceptable to product manufacturer.

B. 	MANUFACTURER’S QUALIFICATIONS: Manufacturer to have minimum (5) five years successful experience in the fabrication of intensive/critical care doors of the type required for this project. Manufacturer to provide field service representation during installation, approving acceptable installer and approving application method.

C.	CERTIFICATIONS: Manual sliding door systems to be certified in accordance with the following standards:

1.	NFPA 101: Code for Safety to Life from Fire in Buildings & Structures.

D.	OPENING FORCE REQUIREMENTS: Standard slide panels glazed with ¼” tempered glass can be slid open with 8-12 lbs. of force.

1.	Breakaway Requirements: Slide-swing panels shall swing out 90° from any position of slide movement (after

positive latching released) and require no more than 50 lbf. (222 N) of force applied at the strike stile to open.

2. 	Units with breakaway feature are UL listed as an exit way and are compliant with NFPA 101.

1.05 WARRANTIES

A. 	MANUFACTURER'S WARRANTY: Units to be warranted against defect in material and workmanship for a period of one year from the Date of Substantial Completion. Manufacturer's warranty is in addition to, and not a limitation of, other rights owner may have under Contract Documents.

B. 	DISTRIBUTOR'S WARRANTY: 1-year warranty: Labor & transportation charges for defective parts replacement.

1.06 PROJECT CONDITIONS

Field Measurements: Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

1.07 DELIVERY, STORAGE AND HANDLING

A. 	ORDERING AND DELIVERY: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. 	STORAGE AND PROTECTION: Provide protection from exposure to harmful weather conditions and vandalism.

# PART II – PRODUCTS

2.01 MANUFACTURER

Horton Automatics, a division of Overhead Door Corporation, shall manufacture manual slide door(s) of type(s) and size(s) specified on plans and door schedule.

2.02 EQUIPMENT

A.	MANUFACTURED DOOR UNITS: Shall include header with roller track, carrier assemblies, framing jamb(s), sliding door panel and accessories required for complete installation.

1. 	Configuration: Single Slide, Biparting or Telescoping

2. 	Mounting Type: Surface mounted onto face of finished wall.

3. 	Door Type:

a. Type 010 (P-X, X-P & P-X-X-P): Slide panel(s) ‘X’ shall slide alongside wall utilizing floor mounted guide.

b. Type 110 (P-SX, SX-P & P-SX-SX-P): Slide-swing panel(s) ‘SX’ shall slide along wall utilizing floor mounted guide.

c. Telescoping 010T (P-X-X, X-X-P): When unit slides in full open position, maximum slide opening will be approximately 70% of overall package width.

B.	HEADER: Shall be aluminum with removable face plate. Header sizes to be:

1.  4" (102 mm) deep by 2 1/2" (63 mm) high for Types 010 and 110.

a. Optional Profiler® header: 4" (102 mm) deep by 6" (152 mm) high.

2.  7" (178 mm) deep by 2 1/2" (63 mm) high for Telescoping door types.

C.	CARRIER ASSEMBLIES AND HEADER ROLLER TRACK: Carrier assemblies shall support door panels with

minimum four rollers per panel. Rollers will be steel, high quality ball bearing wheels 1-1/4" (32mm) diameter. Anti-Derailing shall be accomplished by means of a continuous aluminum extrusion full length of slide panel travel. Overhead header roller track shall be continuous aluminum, nylon covered, and replaceable.

Telescoping doors will have two separate tracks for sliding panels to travel.

D. 	SLIDE PANEL: Shall be aluminum, 1 3/4" (44mm) deep with narrow stile construction except for medium stile strike rail. Standard bottom rail shall be 4" (102mm) tall. Concealed guides to stabilize bottom of sliding panel. Standard glazing prep to be for 1/4” (6mm) glass.

1. 	Swing-out Feature: Slide-swing panels can swing out 90° with maximum 50 lbs. of force applied at the strike rail. Breakout mechanism shall provide support across full width of the door in normal operating mode. In breakout mode, torsion assembly shall support weight of the door to minimize drop. Units with swingout feature are UL listed as an exit way and are compliant with NFPA 101.

2. 	Total weight limit per panel shall be:

a. 200 lbs. (90.7 kg) for slide panel (non-breakout)

b. 156 lbs. (70.7 kg) for slide-swing panel

3. 	Sliding Panel and Sidelite Options shall be:

a. Prep for glazing up to 1 1/2" (38mm).

b. 6 ½” (165mm), 8” (203mm) or 10” (254mm) bottom rail

c. Intermediate horizontal 2 ¼” (57mm) muntin bar.

E. 	JAMBS/FRAME: Shall be aluminum. Non-strike jamb shall be optional. Jamb dimensions to be:

1.	1 3/4" (44 mm) deep by 4" (102 mm) wide.

2.  1 3/4" (44 mm) deep by 7" (178 mm) wide for Telescoping door.

F. HARDWARE: A recessed pull shall be provided on each side of the sliding panel. No locks required.

Optional hardware:

1. Positive latching: The slide panel shall be provided with positive latch that will latch this panel in place

when closed. A lever handle shall be provided on each side of the sliding panel to unlock the door.

2. 	Raised 1” (25mm) diameter tubular pull

2.03 RELATED WORK REQUIREMENTS

GLASS AND GLAZING: Glass stops, glazing vinyl and setting blocks for field glazing as per Safety Glazing

standard ANSI Z97.1.2.

2.04 MATERIALS, FINISHES AND FABRICATION

A. 	EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:

1. 	Structural Header Sections: Minimum 3/16" (5mm) thickness.

2. 	Structural Frame Sections: Minimum 1/8" (3mm) thickness.

3. 	Structural Panel Sections: Commercial grade.

B. 	FINISHES (for all exposed aluminum surfaces): Shall be one of the following:

1. 	215-R1 Clear: Architectural Class 1 Clear Anodized Coating, AA-MI2C22A41.

2. 	313-R1 Dark Bronze, 312-R1 Light Bronze, or 315-R1 Black: Architectural Class 1 Anodized Coating,        AA-MI2C22A44.

3. 	Special Paint Coating: Color as selected.

4. 	Antimicrobial coating.

C.	PANEL CONSTRUCTION:

1.	Corner block type with 3/16" steel backup plate construction, mechanically secured with minimum of four hardened steel screws. Sash consists of snap-in glass stops, snap-in glazing beads and vinyl gaskets. Gasketing material to be captured in extruded aluminum door panel.

2.	Weather-stripping material captured in extruded aluminum door panel. Door nosing weather-strip to be spring-loaded adjustable astragal type. Surface applied self-adhesive weather-stripping not acceptable.

3.	Slide doors to be supplied with adjustable glass setting block to allow for adjusting of door to meet site conditions eliminating the need for additional shims.

D. 	FRAME CONSTRUCTION: Butt joints, mechanically secured by means of screws & formed aluminum brackets.

PART III - EXECUTION

3.01 EXAMINATION

Site Verification of Conditions: Installer must verify that base conditions acceptable for product installation according to with manufacturer's instructions. Notify the Contractor in writing of conditions detrimental to the proper and timely completion of work. Do not start work until all negative conditions are corrected in a manner acceptable to the installer and manufacturer.

3.02 INSTALLATION

A. 	GENERAL: Install door units plumb, level and true to line, without warp or rack of frames or sash with manufacturer's prescribed tolerances. Provide support and anchor in place.

B. 	DISSIMILAR MATERIALS: Comply with AAMA 101, Appendix Dissimilar Materials by separating aluminum materials and other corrodible surfaces from sources of corrosion or electrolytic action contact points.

3.03 CLEANING, ADJUSTMENT AND PROTECTION

A. 	CLEANING: After installation, installer to take following steps:

1. 	Remove temporary protection of adjacent work areas. Remove construction debris from construction site and legally dispose of debris.

2. 	Repair or replace damaged installed products. Clean product surfaces and lubricate operating equipment for optimum condition and safety.

B. 	ADVISE CONTRACTOR: Of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration (other than normal weathering) at the time of acceptance.

Horton Automatics reserves the right to make product improvements and change specifications without notice.

END OF SECTION