DIVISION 08 - OPENINGS

SECTION 08 42 29.23 SLIDING AUTOMATIC ENTRANCES

Specifier Note: Coordinate and edit articles and paragraphs below to suit project requirements. Add section numbers and titles per CSI "MasterFormat" and specifier's practice. Consult with manufacturer regarding performance requirements for units applicable to project, as well as, related equipment and accessories required.

PART I – GENERAL

1.01 SUMMARY

A. 	WORK INCLUDED: Furnish complete automatic aluminum door system, as specified, that has been manufactured, fabricated and installed as per manufacturer’s criteria without defects, damage or failure.

B. 	RELATED WORK:

1. 	Openings: Division 08, applicable sections.

2. 	Electrical: Division 26, applicable sections.

1.02  REFERENCES

A.  AMERICAN ASSOCIATION OF AUTOMATIC DOOR MANUFACTURERS (AAADM).

B. 	AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI):

1. 	ANSI Z97.1: Safety Glazing Materials Used in Buildings - Methods of Test.

2. 	ANSI A156.10: For Power Operated Pedestrian Doors; Sliding Doors section.

3.	ANSI A156.5: Standard for Auxiliary Locks and Associated Products

C. 	AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM)

1.  B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes.

2.  ASTM E330-02: (Wind load) Standard Test Method for Structural Performance of Exterior Windows, Curtain Walls, and Doors by Uniform Static Air Pressure Difference.

3.  ASTM E283-04: (Air Infiltration) Standard test method for rate of air leakage through exterior windows, curtain walls, and doors.

D. 	BUILDING OFFICIALS AND CODE ADMINISTRATORS INTERNATIONAL (BOCA)

E.	INTERNATIONAL CONFERENCE OF BUILDING OFFICIALS / UNIFORM BUILDING CODE (ICBO/UBC)

F.	International Code Council / International Building Code (ICC/IBC)

G. 	NATIONAL FIRE PROTECTION ASSOCIATION (NFPA) 101: Safety to Life from Fire in Buildings & Structures.

H. 	THE ALUMINUM ASSOCIATION (AA) Aluminum Finishes Manual.

I. 	INTERTEK, WARNOCK HERSEY (ETL): Testing Laboratory and Certification Agency joined with ETL SEMKO

J. 	UNDERWRITERS LABORATORY, INC. (USA & CANADA) UL 325: Electrical Door, Drapery, Gate, Louver, and Window Operators and Systems.

1.03  SUBMITTALS

A. 	SHOP DRAWINGS & PRODUCT DATA: Submit drawings and product data showing layout, profiles, product components including anchorage, accessories, finish and glazing details (where required).

B. 	CLOSEOUT SUBMITTALS: Submit the following:

1. 	Owner’s Manual & Warranty document as specified herein.

2. 	AAADM inspection compliance form completed and signed by certified AAADM inspector prior to doors being placed in operation as proof of compliance with ANSI A156.10.

1.04  QUALITY ASSURANCE AND PERFORMANCE REQUIREMENTS

A. 	INSTALLERS QUALIFICATIONS: Installer shall be factory trained, certified by AAADM, and experienced to perform work of this section.

B. 	MANUFACTURER’S QUALIFICATIONS: Manufacturer to have minimum (5) five years successful experience in the fabrication of automatic doors of the type required for this project. Manufacturer capable of providing field service representation during installation, approving acceptable installer and approving application method.

C.	CERTIFICATIONS: Automatic sliding door systems and options shall be factory certified to meet performance design criteria in accordance with the following standards:

1.	ANSI A156.10: For Power Operated Pedestrian Doors; Sliding Doors section.

2.	NFPA 101: Code for Safety to Life from Fire in Buildings & Structures.

3.	ETL Listed: Tested to UL 325 Standard

4.	BOCA: Means of Egress, Power Operated Doors

5.	ICBO/UBC: Egress Through Lobbies

6.	ICC/IBC: Egress Section

D.	OPERATING RANGE: -30° F to 130° F (-34° C to 54° C)

E. 	OPENING FORCE REQUIREMENTS FOR Emergency Egress:

1. 	Slide-swing panels shall require no more than 50 lbf. (222 N) of force to swing open. Slide-swing panels shall be capable of swinging out 90° from any position of slide movement.

2. 	Slide-swing panels shall have torsion spring designed to re-close panel if pushed open in the direction of egress. Total weight of ETL listed slide-swing panel shall not exceed 156 lbs. (70.7 kg).

3. 	If power fails, slide panels can be manually slid open with no more than 15 lbf (222 N) of force.

4. 	Units are ETL listed as an exit way and are compliant with NFPA 101.

F. 	CLOSING FORCE REQUIREMENTS: Maximum force required to prevent sliding panel from closing = 28 lbf. (124.5 N) Adjustable Reversing Circuit will reopen door unit if closing path is obstructed.

G.	HEADER CAPACITY: Header shall be capable of supporting:

1.	Biparting: Up to 250 lbs. (113.4 kg) per slide panel over spans up to 16’-0” (4877mm) without intermediate supports.

2.	Single Slide: Up to 350 lbs. (158.7 kg) per slide panel over spans up to 9’-0” (2743mm) without intermediate supports

H.	WIND LOAD: Structural Performance per ASTM E330-02: Measured +/-40 psf with no glass breakage.

I.	AIR INFILTRATION: per ASTM E283-04: Standard Test Pressure @ 1.57 psf, Measured 1.36 cfm/ft²

1.05  WARRANTIES

A. 	MANUFACTURER'S WARRANTY: Units to be warranted against defect in material and workmanship for a period of one year from the Date of Substantial Completion.

Manufacturer's warranty is in addition to, and not limited to, other rights owner may have under Contract Documents.

B. 	DISTRIBUTOR'S WARRANTY: 1 year warranty: Labor/ transportation charges for defective parts replacement.

1.06  PROJECT CONDITIONS

Field Measurements: Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

1.07 DELIVERY, STORAGE AND HANDLING

A. 	ORDERING AND DELIVERY: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. 	STORAGE AND PROTECTION: Provide protection from exposure to harmful weather conditions and vandalism.

PART II – PRODUCTS

2.01 MANUFACTURER

Horton Automatics, a division of Overhead Door Corporation, shall manufacture automatic sliding door(s) of type(s) and size(s) specified on plans and door schedule.

2.02  EQUIPMENT

A. 	MANUFACTURED DOOR UNITS: Shall include operator, header with roller track, carrier assemblies, framing, sliding door panel, sidelite, activation, safety devices and accessories required for complete installation.

1.	Configuration: Biparting

2.	Mounting Type: Perimeter mounted within rough opening

3. 	Door Type: Type 310: Slide-swing panels ‘SX’ shall slide along swing-out sidelites ‘SO’.

B.	OPERATOR: The operator shall be mounted and concealed within the header. Maximum current draw shall not exceed 3.15 amps.

1. 	The standard electric operating mechanism shall be the Series Profiler® Elite Belt Drive electric operating mechanism. Operating force shall be accomplished through a 1/8 HP DC permanent magnet motor with worm gear transmission and 1800 RPM working with drive belt, attached door hangers, and idler pulley. Drive belt to be steel reinforced nylon, 1/2" (13 mm) wide. Idler pulley to be reinforced, metallic material.

2.	Microprocessor-based control shall include a 40 character alphanumeric display to provide ease of adjustment and comprehensive diagnostics, including error and alarm logging. All speeds, forces and time delays shall be independently adjustable. Actuating and safety sensors that provide self-monitoring are supported. Supported operating modes include 2-Way Automatic / 1-Way Exit, Full / Reduced Door Opening, and Day / Night Operation.

3.  Finger Safety: Strike rail of sliding panel will stop short of adjacent sidelite; resulting opening is net slide.

4. 	On/Off Switch shall be supplied. When switched OFF, unit reverts to free manual operation (likewise during electrical power failure).

C. 	Security and Safety Power Fail Options:

1. 	Automatic lock: Automatically locks slide function of door when in closed position. Additional power supply for autolock not acceptable.

a. 	Autolock Fail Secure: If power fails the lock engages.

b. 	Autolock Fail Safe: If power fails the lock disengages.

2. 	Monitored Power Fail Options (battery back-up):

a. 	Software Selectable Power Fail Open: If power fails the door slides open.

b. 	Software Selectable Power Fail Close: If power fails the door slides closed.

D. 	PROFILER® HEADER: Shall be slim 4" (102mm) deep by 6" (152mm) high aluminum construction with extruded z-profile reinforcement for dead load and lateral strength. Header shall have removable face plate for service and adjustment of operator and controls. Header mounts flush to 4” framing jambs.

E. 	CARRIER ASSEMBLIES AND HEADER ROLLER TRACK: Carrier assemblies shall support door panels with minimum four rollers per panel. Rollers will be steel, high quality ball bearing wheels 1-1/4" (32 mm) diameter. Anti-Derailing shall be accomplished by means of a continuous aluminum extrusion full length of slide panel travel. Overhead header roller track shall be continuous aluminum, nylon covered, and replaceable.

F. 	SLIDING PANELS AND SIDELITES: Shall be aluminum, 1-3/4" (44 mm) deep with narrow stile rails. An intermediate, horizontal rail (muntin bar), 2 1/4” (57 mm) wide, shall be furnished for safety and division of glass . Standard bottom rail shall be 4" (102mm) tall. Sliding panels shall have concealed bottom guides to stabilize slide travel.

1. 	Weather-stripping: Along perimeter of sliding panels and swing-out sidelites. Weatherstripping material captured in extruded aluminum door panel. Surface applied self-adhesive weatherstripping not acceptable. Adjustable spring-loaded double astragal weather-stripping at lead edge, double mohair at interlock rails.

2.	Standard glazing prep to be for 1/4” (6 mm) glass.

3.	Sliding Panel and Sidelite Options shall be:

a.	Medium stile construction: 3 3/4” (95mm) wide vertical rails with 6 1/2” (165mm) tall bottom rail.           Note: Medium stile construction will reduce slide opening.

b.	Wide stile construction: 5” (127mm) wide vertical rails with 6 1/2” (165mm) tall bottom rail.                   Note: Wide stile construction will reduce slide opening.

G. 	BREAKOUT PANELS: Slide-swing panels can swing out min.90° from any position of slide movement and require no more than 50 lbf. (222 N) of force applied at the lock stile to open.

1. 	Slide-swing panels shall have torsion spring designed to re-close panel if pushed open in the direction of egress.

2. 	Breakout mechanism shall provide support across full width of the door, in normal operating mode. In breakout mode, torsion assembly shall support weight of the door to minimize drop during emergency egress. Total weight of ETL listed slide-swing panel shall not exceed 156 lbs. (70.7 kg).

3. 	Slide-swing panels shall include intermediate horizontal rail.

4. 	Units with breakout feature are ETL listed as an exit away and are compliant with NFPA 101.

H. 	JAMBS/FRAME: Shall be aluminum. Jamb dimensions to be:

1. 	1 3/4" (44mm) deep by 4" (102mm) wide.

I. 	THRESHOLD: Shall be aluminum, 1/2" (25 mm) tall by 4” (102 mm) wide.

J.	HARDWARE: ANSI A156.5, Grade 1, 4-Point Locking provided and installed in strike rail shall include:

1.	5/8” Hookbolt Lock latching into adjacent strike rail.

2.	Maximum Security Lock with 31/32" (25 mm) backset.

3.	Keyed Cylinder mounted on exterior side with 1 5/32" (29 mm) standard size cylinder.

4.	Thumbturn mounted on interior side.

5.	3/8” Lockbolt into breakout carrier frame and threshold.

2.03  RELATED EQUIPMENT

BASIC SENSOR SYSTEM: Shall be 24 VDC, class ll circuit and shall be adjusted and installed in compliance with ANSI A156.10. System shall include the following:

A.	 ACTIVATION SENSORS: Microwave or active infrared sensor shall be header-mounted each side of door unit for detection of traffic from each direction.

B. 	Threshold presence sensors:

1. 	Header mounted sensors shall provide active infrared presence detection on each side of the door unit and shall remain active throughout the entire door opening and closing cycle.

2. 	Hold-open beams: Two pulsed infrared photoelectric beams to be mounted in vertical rails of sidelite or in jambs. Sender/receiver arrangement parallels door opening.

2.04  RELATED WORK REQUIREMENTS

A. 	ELECTRICAL: 120 VAC, 50/60 cycle, single phase, dedicated 20 amp circuit per operator. Non-North American voltages can be 240 VAC 50/60 cycle (operator must have 240 volt power supply).

B. 	GLASS AND GLAZING: Glass stops, glazing vinyl and setting blocks for field glazing as per Safety Glazing standard ANSI Z97.1.2. Contractor to coordinate acquisition of glass in thickness and type in accordance with manufacturer's recommendations for prescribed design.

2.05  MATERIALS, FINISHES AND FABRICATION

A. 	EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:

1. 	Structural Header Sections: Minimum 3/16" (5 mm) thickness.

2. 	Structural Frame Sections: Minimum 1/8" (3 mm) thickness.

3. 	Structural Panel Sections: Commercial grade.

B. 	FINISHES (for all exposed aluminum surfaces): Shall be one of the following:

1. 	215-R1 Clear: Arch. Class 1 Clear Anodized Coating, AA- MI2C22A44.

2. 	313-R1 Dark Bronze: Arch. Class 1 Anodized Coating, AA-MI2C22A44.

3. 	312-R1 Medium Bronze: Arch. Class 1 Anodized Coating, AA-MI2C22A44.

4. 	311-R1 Light Bronze: Arch. Class 1 Anodized Coating, AA-MI2C22A44.

5. 	Champagne: Arch. Class 1 Anodized Coating, AA-MI2C22A44.

6. 	Gold: Arch. Class 1 Anodized Coating, AA-MI2C22A44.

7. 	Paint Coating:

a.	Powder Coat: 100% V.O.C. free fluoropolymer resin-based. Standard and custom colors available including wood grain finish.

b.	Wet Paint: Standard and custom colors available.

8. 	Clad with stainless steel or muntz metal (brass alloy): #4 brushed finish.

C.	PANEL CONSTRUCTION:

1.	Corner block type with 3/16” steel backup plate construction, mechanically secured with minimum of four hardened steel screws. Sash consists of snap-in glass stops, snap-in glazing beads and vinyl gaskets.

2.	Slide-swing doors to be supplied with adjustable glass setting block to allow for adjusting of door to meet site conditions eliminating the need for additional shims.

D. 	FRAME CONSTRUCTION: Butt joints, mechanically secured with screws and formed alum. corner brackets.

E. 	OPERATOR CONSTRUCTION: Electromechanical, modular type construction.

PART III - EXECUTION

3.01  EXAMINATION

SITE VERIFICATION OF CONDITIONS: Installer must verify that base conditions are acceptable for product installation according to with manufacturer's instructions. Notify the Contractor in writing of conditions detrimental to the proper and timely completion of work. Do not start work until all negative conditions are corrected.

3.02  INSTALLATION

A. 	GENERAL: Installer shall be factory trained, certified by AAADM, and experienced to perform work of this section. Install door units plumb, level and true to line, without warp or rack of frames or sash with manufacturer's prescribed tolerances. Provide support and anchor in place. Provide weather-tight construction.

B. 	ELECTRICAL: General or electrical contractor to install all wiring to operator on a separate circuit breaker routed into header. General or electrical contractor also to install all necessary power and low voltage wiring for proper operation of associated security systems.

3.03  CLEANING, ADJUSTMENT AND PROTECTION

A. 	CLEANING: After installation, installer will clean product surfaces and lubricate operating equipment for optimum condition and safety. Advise contractor of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration at the time of acceptance.

B. 	ADJUSTMENT: AAADM certified technician to inspect and adjust installation. Comply with ANSI A156.10.

Note: Horton Automatics reserves the right to make product improvements and change specifications without notice.

END OF SECTION