DIVISION 08 - OPENINGS

SECTION 08 42 29.23 SLIDING AUTOMATIC ENTRANCES

Specifier Note: Coordinate and edit articles and paragraphs below to suit project requirements. Add section numbers and titles per CSI "MasterFormat" and specifier's practice. Consult with manufacturer regarding performance requirements for units applicable to project, as well as, related equipment and accessories required.

PART I – GENERAL

1.01 SUMMARY

A. 	WORK INCLUDED: Furnish complete automatic aluminum door system, as specified, that has been manufactured, fabricated and installed as per manufacturer’s criteria without defects, damage or failure.

B. 	RELATED WORK:

1. 	Concrete: Division 03, applicable sections.

2.  Masonry: Division 04, applicable sections.

3. 	Openings: Division 08, applicable sections.

4. 	Electrical: Division 26, applicable sections.

1.02  REFERENCES

A.  AMERICAN ASSOCIATION OF AUTOMATIC DOOR MANUFACTURERS (AAADM).

B. 	AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI):

1. 	ANSI Z97.1: Safety Glazing Materials Used in Buildings - Methods of Test.

2. 	ANSI A156.10: For Power Operated Pedestrian Doors; Sliding Doors section.

3.	ANSI A156.5: Standard for Auxiliary Locks and Associated Products

C. 	AMERICAN SOCIETY FOR TESTING AND MATERIALS (ASTM) B221: Aluminum-Alloy Extruded Bars, Rods, Shapes and Tubes.

D. 	BUILDING OFFICIALS AND CODE ADMINISTRATORS INTERNATIONAL (BOCA)

E.	INTERNATIONAL CONFERENCE OF BUILDING OFFICIALS / UNIFORM BUILDING CODE (ICBO/UBC)

F.	International Code Council / International Building Code (ICC/IBC)

G. 	NATIONAL FIRE PROTECTION ASSOCIATION (NFPA) 101: Safety to Life from Fire in Buildings & Structures.

H. 	THE ALUMINUM ASSOCIATION (AA) Aluminum Finishes Manual.

I. 	INTERTEK, WARNOCK HERSEY (ETL): Testing Laboratory and Certification Agency joined with ETL SEMKO

J. 	UNDERWRITERS LABORATORY, INC. (USA & CANADA) UL 325: Electrical Door, Drapery, Gate, Louver, and Window Operators and Systems.

1.03  SUBMITTALS

A. 	SHOP DRAWINGS & PRODUCT DATA: Submit drawings and product data showing layout, profiles, product components including anchorage, accessories, finish and glazing details (where required).

B. 	CLOSEOUT SUBMITTALS: Submit the following:

1. 	Owner’s Manual & Warranty document as specified herein.

2. 	AAADM inspection compliance form completed and signed by certified AAADM inspector prior to doors being placed in operation as proof of compliance with ANSI A156.10.

1.04  QUALITY ASSURANCE AND PERFORMANCE REQUIREMENTS

A. 	INSTALLERS QUALIFICATIONS: Installer shall be factory trained, certified by AAADM, and experienced to perform work of this section.

B. 	MANUFACTURER’S QUALIFICATIONS: Manufacturer to have minimum (5) five years successful experience in the fabrication of automatic doors of the type required for this project. Manufacturer capable of providing field service representation during installation, approving acceptable installer and approving application method.

C.	CERTIFICATIONS: Automatic sliding door systems and options shall be factory certified to meet performance design criteria in accordance with the following standards:

1.	ANSI A156.10: For Power Operated Pedestrian Doors; Sliding Doors section.

2.	NFPA 101: Code for Safety to Life from Fire in Buildings & Structures.

3.	ETL Listed: Tested to UL 325 Standard

4.	BOCA: Means of Egress, Power Operated Doors

5.	ICBO/UBC: Egress Through Lobbies

6.	ICC/IBC: Egress Section

D.	OPERATING RANGE: -30° F to 130° F (-34° C to 54° C)

E. 	OPENING FORCE REQUIREMENTS FOR Emergency Egress:

1. 	Slide-swing panels shall require no more than 50 lbf. (222 N) of force to swing open. Slide-swing panels shall be capable of swinging out 90° from any position of slide movement.

2. 	Slide-swing panels shall have torsion spring designed to re-close panel if pushed open in the direction of egress. Total weight of ETL listed slide-swing panel shall not exceed 156 lbs. (70.7 kg).

3. 	If power fails, slide panels can be manually slid open with no more than 15 lbf (222 N) of force.

4. 	Units are ETL listed as an exit way and are compliant with NFPA 101.

F. 	CLOSING FORCE REQUIREMENTS: Maximum force required to prevent sliding panel from closing = 28 lbf. (124.5 N) Adjustable Reversing Circuit will reopen door unit if closing path is obstructed.

G.	HEADER CAPACITY: Header shall be capable of supporting:

1.	Biparting: Up to 300 lbs. (136 kg) per slide panel over spans up to 16’-0” (4877mm) without intermediate supports.

2.	Single Slide: Up to 500 lbs. (227 kg) per slide panel over spans up to 9’-0” (2743mm) without intermediate supports

1.05  WARRANTIES

A. 	MANUFACTURER'S WARRANTY: Units to be warranted against defect in material and workmanship for a period of one year from the Date of Substantial Completion.

Manufacturer's warranty is in addition to, and not limited to, other rights owner may have under Contract Documents.

B. 	DISTRIBUTOR'S WARRANTY: 1 year warranty: Labor/ transportation charges for defective parts replacement.

1.06  PROJECT CONDITIONS

Field Measurements: Verify actual dimensions/openings by field measurements before fabrication and record on shop drawings. Coordinate with fabrication and construction schedule to avoid construction delays.

1.07 DELIVERY, STORAGE AND HANDLING

A. 	ORDERING AND DELIVERY: Comply with factory's ordering instructions and lead time requirements. Delivery shall be in factory's original, unopened, undamaged containers with identification labels intact.

B. 	STORAGE AND PROTECTION: Provide protection from exposure to harmful weather conditions and vandalism.

PART II – PRODUCTS

2.01 MANUFACTURER

Horton Automatics, a division of Overhead Door Corporation, shall manufacture automatic sliding door(s) of type(s) and size(s) specified on plans and door schedule.

2.02  EQUIPMENT

A. 	MANUFACTURED DOOR UNITS: Shall include operator, header with roller track, carrier assemblies, framing, sliding door panel, sidelite, activation, safety devices and accessories required for complete installation.

1.	Configuration: Single Slide or biparting

2.	Mounting Type:

a.	Perimeter mounted within rough opening

b.	Surface mounted

3. 	Door Type:

a.	Type 010: Sliding panel(s) ‘X’ shall slide along fixed sidelite(s) ‘O’ or wall ‘P’.

b. 	Type 110: Slide-swing panel(s) ‘SX’ shall slide along sidelite(s) ‘O’ or wall ‘P’.

B.	OPERATOR: The Electric Operating Mechanism shall be HD-Slide® Series 2001 Belt Drive. Maximum current draw shall not exceed 3.15 amps. The heavy duty operator shall be mounted and concealed within the header.

1. 	Operating force shall be accomplished through a 1/8 HP DC permanent magnet motor with heavy duty worm gear transmission and 1800 RPM working with reinforced drive belt, attached 1/4” thick steel door hangers, and idler pulley (1/4 HP motor required for door panels weighing 500 lbs). Drive belt to be steel reinforced nylon, 1" (25.4 mm) wide. Idler pulley to be reinforced, metallic material.

2.	Microprocessor-based control shall include a 40 character alphanumeric display to provide ease of adjustment and comprehensive diagnostics, including error and alarm logging. All speeds, forces and time delays shall be independently adjustable. Actuating and safety sensors that provide self-monitoring are supported. Supported operating modes include 2-Way Automatic / 1-Way Exit, Full / Reduced Door Opening, and Day / Night Operation.

3.  Finger Safety: Strike rail of sliding panel will stop short of adjacent sidelite; resulting opening is net slide.

4. 	On/Off Switch shall be supplied. When switched OFF, unit reverts to free manual operation (likewise during electrical power failure).

C. 	Security and Safety Power Fail Options:

1. 	Automatic lock: Automatically locks slide function of door when in closed position. Additional power supply for autolock not acceptable.

a. 	Autolock Fail Secure: If power fails the lock engages.

b. 	Autolock Fail Safe: If power fails the lock disengages.

2. 	Monitored Power Fail Options (battery back-up):

a. 	Software Selectable Power Fail Open: If power fails the door slides open.

b. 	Software Selectable Power Fail Close: If power fails the door slides closed.

D. 	HD-Slide® HEADER: Shall be 6" (152 mm) deep by 8" (203 mm) high, heavy duty aluminum construction with removable face plate and extruded support brackets for dead load and lateral strength.

E. 	CARRIER ASSEMBLIES AND HEADER ROLLER TRACK: Carrier assemblies shall support door panels with minimum four rollers per panel. Rollers will be non-metallic high quality ball bearing wheels 2" (51 mm) diameter. Anti-Derailing shall be accomplished by means of a continuous aluminum extrusion full length of slide panel travel. Overhead header roller track shall be continuous aluminum and replaceable.

F. 	SLIDING PANEL(S) AND SIDELITE(S): Flush Stainless Steel: Non-corrosive, heavy duty panel shall have a structural core of resin impregnated Kraft honeycomb with 18 ga. #4 stainless steel exterior skins. Interior framing shall be extruded 6063T-5 anodized extruded aluminum alloy no less than .09” (2mm) thick. The panel shall present a flush appearance with no exposed fasteners. Nominal panel thickness shall be 1-3/4" (44mm). Sliding panel shall be provided with flush pull(s) and shall have concealed bottom guides to stabilize slide travel.

1. 	Weather-stripping: Captured in extruded interior aluminum framing. Surface applied self-adhesive weatherstripping not acceptable. Adjustable spring-loaded double astragal with double neoprene weather-strip at lead edge, neoprene at interlock area and sidelite/Jamb joint.

2.	Optional Vision Lites: Glazing prep. from 1/4” (6mm) to 1” (25mm).

a. Square & centered on sliding panel. 10” (254mm) - 24" (610mm) Square.

b. Rectangular & off-center, min. 3 ¾” from slide door edge. Min. 3” wide x 10” (254mm) - 24" (610mm) tall.

G. 	BREAKOUT PANELS: Slide-swing panels can swing out min.90° from any position of slide movement and require no more than 50 lbf. (222 N) of force applied at the lock stile to open.

1. 	Slide-swing panels shall have torsion spring designed to re-close panel if pushed open in the direction of egress.

2. 	Breakout mechanism shall provide support across full width of the door, in normal operating mode. In breakout mode, torsion assembly shall support weight of the door to minimize drop during emergency egress. Total weight of ETL listed slide-swing panel shall not exceed 156 lbs. (70.7 kg).

3. 	Slide-swing panels shall include intermediate horizontal rail.

4. 	Units with breakout feature are ETL listed as an exit away and are compliant with NFPA 101.

H. 	JAMBS/FRAME: Shall be aluminum 1 3/4" (44 mm) deep by 4" (102 mm) wide. Exhaust hole shall be provided at bottom of frame to exhaust any particles generated by motor or drive system.

I. 	OPTIONAL LOCKING HARDWARE: ANSI A156.5, Grade 1, 2-Point Locking provided and installed in interior strike rail framing shall include:

1. 	Hookbolt Latch, 5/8” laminated stainless steel, latching into jamb or adjacent strike rail.

2. 	3/8” hex-bolt into breakout carrier frame.

3. 	Keyed 1 5/32" (29 mm) Cylinder mounted on exterior side with 31/32" (25 mm) backset

4. 	Thumbturn mounted on interior side.

2.03  RELATED EQUIPMENT

A. 	ACTIVATING DEVICE: Shall be 24 VAC, class ll circuit. Actuator to be located on each side of the opening for 2-way traffic. Standard actuator shall be Motion Sensor mounted above opening on header or wall.

Optional activating devices shall be one of the following:

1.	Touchless Switch: 1 11/16” (43mm) x 4 1/2” (114mm), Wall or jamb mounted using diffused scanning technology with adjustable range up to 30". Junction box included.

2. 	Rectangular Push Plate Switch: 1 1/2” (38mm) x 4 1/2” (114mm), Momentary contact switch with plain stainless steel plate. Junction box included.

3. 	Push Plate Wall Switch: Momentary contact switch, 6 1/4” (159 mm) dia. stainless steel plate on standard junction box.

B. 	Threshold presence sensors:

1. 	Header mounted sensors shall provide active infrared presence detection on each side of the door unit and shall remain active throughout the entire door opening and closing cycle.

2. 	Hold-open beams: Two pulsed infrared photoelectric beams to be mounted in vertical rails of sidelite or in jambs. Sender/receiver arrangement parallels door opening.

C. OPTIONAL INTERLOCK CONTROLLER: Multiple doors entering a clean room and/or vestibule area shall include a microprocessor based interlock control to prevent two doors from being open at the same time. The control shall keep track of the order of request from the activation switch. Design shall control up to eight doors and shall have a memory capable of remembering order of open requests.

2.04  RELATED WORK REQUIREMENTS

A. 	ELECTRICAL: 120 VAC, 50/60 cycle, single phase, dedicated 20 amp circuit per operator. Non-North American voltages can be 240 VAC 50/60 cycle (operator must have 240 volt power supply).

B. 	GLASS AND GLAZING: Glazing vinyl and setting blocks for field glazing as per Safety Glazing standard ANSI Z97.1.2. Contractor to coordinate acquisition of glass in thickness and type in accordance with manufacturer's recommendations for prescribed design.

2.05  MATERIALS, FINISHES AND FABRICATION

A. 	EXTRUDED ALUMINUM: ASTM B221, 6063-T5 alloy and temper, anodized:

1. 	Structural Header Sections: Minimum 3/16" (5 mm) thickness.

2. 	Structural Frame Sections: Minimum 1/8" (3 mm) thickness.

3. 	Structural Panel Sections: Commercial grade.

B. 	FINISHES (for all exposed surfaces): Shall be clad with stainless steel, #4 brushed finish.

C.	PANEL CONSTRUCTION: Corner block type with 3/16” steel backup plate construction, mechanically secured with minimum of four hardened steel screws. See also to Section 2.02, paragraph ‘F.’

D. 	FRAME CONSTRUCTION: Butt joints, mechanically secured with screws and formed alum. corner brackets.

E. 	OPERATOR CONSTRUCTION: Electromechanical, modular type construction.

PART III - EXECUTION

3.01  EXAMINATION

SITE VERIFICATION OF CONDITIONS: Installer must verify that base conditions are acceptable for product installation according to with manufacturer's instructions. Notify the Contractor in writing of conditions detrimental to the proper and timely completion of work. Do not start work until all negative conditions are corrected.

3.02  INSTALLATION

A. 	GENERAL: Installer shall be factory trained, certified by AAADM, and experienced to perform work of this section. Install door units plumb, level and true to line, without warp or rack of frames with manufacturer's prescribed tolerances. Provide support and anchor in place. Provide weather-tight construction.

B. 	ELECTRICAL: General or electrical contractor to install all wiring to operator on a separate circuit breaker routed into header. General or electrical contractor also to install all necessary power and low voltage wiring for proper operation of associated security systems.

3.03  CLEANING, ADJUSTMENT AND PROTECTION

A. 	CLEANING: After installation, installer will clean product surfaces and lubricate operating equipment for optimum condition and safety. Advise contractor of precautions required through the remainder of the construction period, to ensure that doors will be without damage or deterioration at the time of acceptance.

B. 	ADJUSTMENT: AAADM certified technician to inspect and adjust installation. Comply with ANSI A156.10.

Note: Horton Automatics reserves the right to make product improvements and change specifications without notice.

END OF SECTION